## Slide 1: Author: Craig Harrison Managing Director, I S Systems Pty Limited
Power System Stability & Efficiency Improvements through DC Techniques
PPA Conference, 1st to 5th August 2016

## Slide 2
Medium Utility Scale - Problems Needing Solutions
2. Flexible Generation - Minimum Spinning Reserve & Dynamic Behaviour
- example
3 Network Management & Stability - DC Interconnectivity
- example
Presentation Outline

## Slide 3
Conference Theme - Network & RE
Integration Problems
Maintaining Higher Load Factors
Reducing Spinning Reserve
Reducing Cyclic Operation of Conventional Generation
Minimising RE Spillage in the Absence of Storage
Increasing Efficiency & Reduced Fuel Consumption

## Slide 4
Network & RE Integration Problems
"We cannot solve our problems
using the same thinking
we used to create them"
Albert Einstein
DC Techniques Offer an Alternative Approach

## Slide 5
Review of Studies
Network Stability & Variable RE Studies suggest “standard solutions”!
Variable DE generation is not considered
Networks & Generation segmentation is not considered

## Slide 6
Existing Generator Sets
conversion to
Flexible & Dynamic “Hybrid Generators”
Topic 1

## Slide 7
Variable Speed Generation!
VS
Generation
Power Flow
open
closed
closed
Spinning
Reserve
Set

## Slide 8
How Does this Work?
Step 1: Spinning Reserve Set (off bus) is idling at say 50 % Speed
&
Inverter is on-line & lightly loaded, say 200 kW
Step 2: Station load rapidly increasing above the base load
(e.g. loss of PV)
Step 3: Inverter instantly starts delivering power from generator via the
DC rectifier - independent of volts and frequency and the DC link capacitors
Step 4: Generator engine is accelerated – increasing the available power
to match the increasing load – less than 10 s response
(0 to 100 % power)
Step 5: Excess load reduces – engine speed reduced

## Slide 9
Typical Solar Data (Source: UQ)
A Nearly Perfect Day!

## Slide 10
Typical Solar Data (Source: UQ)
A More Typical Day …

## Slide 11
Typical Solar Data (Source: UQ)
A Month in January 2016

## Slide 12
Variable Speed Generation
Fast Response
Spinning reserve Genset is online – No starting or synchronising time
Reduced fuel consumption – Spinning reserve
Facilitates higher load factor – Security without burning more fuel
Ramp rate smoothing option with large DC link capacitors
Online Inverter can function as a static VAR generator – Reduced VAR
demand on generators – Higher load factors

## Slide 13
Engine & Generation Characteristics
Load
(kW)
Speed (RPM)
Specific
Fuel
Consumption
Contours
(g/kWh)
1500 kW,
1800 RPM
Engine
Example Only
Power = f(n3)

## Slide 14
Engine & Generation Characteristics
Load
(kW)
1500 kW,
1800 RPM
Engine
Example Only
~ 305 g/kWh
@
100 % Speed
Speed (RPM)

## Slide 15
Engine & Generation Characteristics
Load
(kW)
1500 kW,
1800 RPM
Engine
Example Only
~ 305 g/kWh
@
100 % Speed
Speed (RPM)
~ 218 g/kWh
@
50 % Speed

## Slide 16
Diesel Fuel Density  832 g/L
100 % Speed @ ~ 10 % Base Load (200 kW)
50 % Speed @ ~ 10 % Base Load (200 kW)
29 % Fuel saving by dropping to 50 % speed at low load
Engine & Generation Characteristics

## Slide 17
1,500kW Set - Savings at Low Utilisation
(approx. 10 hrs per day)

## Slide 18
1,500kW Set - Savings at High Utilisation
(approx. 22 hrs per day)

## Slide 19
Commercial Considerations
System cost will vary according to the engine, power required, utilization
& specific site specifics
System life expectancy  20 years +
Cost Recovery Time typically – 4 to 6 years

## Slide 20
Slow Speed Running - Impact on the Engine
Quotes from Caterpillar:
“The most prevalent consequence of under loading is exhaust manifold
slobber, or wet stacking”
“Long periods of light loading can lead to deposit build-up behind the
piston rings or inside the cylinders”
Marine Engines:
Extensively studied and managed
Solution:
Generation scheduling to load sets for short periods
Fan control for correct temperature operation

## Slide 21
MV Inverter VSD - Technology
Inverter Cells
Transformer
Image: Delta Electronics, Taiwan

## Slide 22
AC Power Network Stabilisation
with
DC Interconnector Units
Topic 2

## Slide 23
HVDC LINKS – HIGH POWER TRANSMISSION
Established Technology for High Powers
Siemens: Basslink – Victoria & Tasmania
Siemens: Pole 3 – NZ North & South Islands
ABB: HVDC Light

## Slide 24
DC Applied in Electrical Distribution Networks
Presentation by: Dr. R. W. De Doncker, Director
Decoupling of AC Network Segments & Reactive Power Demand
DC Ring Main

## Slide 25
Distribution Network Issues
Increased RE Penetration – Transient Behaviour
Poor Transmission Lines – Fringe of Network
Power Quality – Reactive Power & Voltage Regulation
Network Stability – Reactive Power & Voltage Regulation

## Slide 26
Network Segmentation – DC Interconnector Unit
(back to back inverters)
Ramp Rate Smoothing Capacitor

## Slide 27
No Frequency OR Phase Synchronising Requirements
Network Voltage Regulation
Network Support AND Fault Clearance
DC Interconnector Unit - Features
Bidirectional OR Unidirectional Active Power Flow
Load Transient Smoothing Capacitors
Static VAR Compensator – Import & Export VARs – both sides

## Slide 28
DC Interconnector Unit - Example

## Slide 29
THANK YOU
FOR
YOUR INTEREST