## Slide 1: Lithium-ion batteries in PSOC operation
Jim McDowall
PE/SB Tech Sessions January 10, 2016

## Slide 2: Cycle-life curves
7,500 cycles of 70% DOD
5,250 C throughput
1M cycles of 4% DOD
40,000 C throughput

## Slide 3: Recap of Li-ion basics
Lithium Ion
Metal Ion
Carbon
Oxygen
Separator
POSITIVE
NEGATIVE
SEI
e–
Charge
Charge
Discharge
e–
Discharge

## Slide 4: Li-ion technology choices
Family of electrochemical systems
Positive electrode
  Metal-oxides (e.g. NMC, NCA)
  Phosphates (e.g. LFP)
Negative electrode
  Graphite & other carbons
  Lithium-titanate

## Slide 5: Li-ion technology choices
High cell
voltage
Low cell
voltage

## Slide 6: Li-ion technology choices
Forms
SEI
No
SEI

## Slide 7: Li-ion technology choices
Height of block indicates ‘slope’
Technologies with ‘slope’
are easier to balance in PSOC operation

## Slide 8: PSOC cycling application characteristics
Cell voltage (battery cost/kWh)
Slope of OCV vs SOC
Asymmetry of charge and discharge power (and whether it matters)
Power vs. energy considerations
Cycle life

## Slide 9: Application analysis
PV ramp-rate control
PJM regulation signals

## Slide 10: PV ramp-rate control
Anatomy of a ramp
  PV grid-connection standards
Upward vs. downward ramps
  Clipping of PV inverter output during upward ramps

## Slide 11: PJM regulation signals
Symmetrical operation!
RegD vs RegA
  RegD fast & low energy
  RegA slow & high energy
Reg purchases approx. 1% of load
  <=40% RegD
ESS resources reaching saturation
  Some grid events need more energy
New hybrid signal?
  Fast & higher energy

## Slide 12: Questions?
jim.mcdowall@saftbatteries.com